## Assessment
Risk assessment
Work description
Site / location
Date
Assessed by
Reviewed by (not doing the work)
Risk owner
Accepted (name, date)
ID | What can go wrong | Worst consequence area | Likelihood | Consequence | Score | Level | Controls in place on the day | Likelihood after | Consequence after | Score after | Level after | Stop conditions | Action owner | Due | Accepted by
1 | UPS to maintenance bypass (MOP-UPS-001): the utility fails while the load is on maintenance bypass. The IT load drops until the generators take over. | Service and load | 2 | 5 |  |  | Planned window, no storms forecast, no known grid work; generators checked and in automatic; exposure window as short as possible; switching sequence rehearsed so the way back is quick. | 1 | 5 |  |  | As in MOP-UPS-001. |  |  | Risk owner, in writing
2 | Planned utility transfer test (MOP-PWR-002): cooling is slow to restart after the transfer to generator, and data hall temperatures pass their limit. | Service and load | 3 | 3 |  |  | Pumps and CRAH fans on their own UPS; chiller restart time known from the last test; test done in cool weather. | 2 | 3 |  |  | Data hall temperature reaches the agreed limit. |  |  | Facility manager
3 | Vendor work in a data hall (SOP-SEC-003): the vendor works on the wrong rack or pulls the wrong cable, and drops customer equipment. | Service and load | 3 | 4 |  |  | Work approval names the rack and asset tags; label checked against the approval before anything is touched; escort from operations stays for work on critical equipment. | 2 | 4 |  |  | The asset or its state can't be confirmed. |  |  | Facility manager
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
Score = likelihood × consequence. Severity rule: a consequence of 5 is never below High. Scales and matrix: see the Scales and Matrix sheets.

## Scales
Scales
Likelihood
How likely is it that this happens during this work, or in this period?
Level | Likelihood | What it means
1 | Very unlikely | Not seen in this kind of work. It would take several failures at once.
2 | Unlikely | It has happened in the industry, but nobody expects it here.
3 | Possible | It has happened on sites like this one. It could happen this time.
4 | Likely | Expected at some point if nothing changes.
5 | Almost certain | Already happening, or will happen without action.
Consequence
Score all four columns and use the worst one.
Level | People | Service and load | Equipment | Cost
1 | No injury | No effect | No damage | Negligible
2 | First aid | One redundant component lost, no load affected | Minor repair | Covered by the normal operating budget
3 | Medical treatment | A system runs without redundancy, or margins near their limits (temperature, battery time) | Component replaced | Needs approval outside the budget
4 | Serious injury | Load dropped in any room, critical or not, or for some customers | Major unit damaged, long repair | Large unplanned cost, or contract penalties
5 | Fatality or life-changing injury | Load dropped across the site or for many customers | Major system destroyed, or fire | Threatens the contract, the customer or the business
Note: The site sets the amounts for each cost level. Cost alone can raise the consequence: a repair bill or contract penalty at level 4 makes it a 4, even if no load was lost.

## Matrix
Risk matrix
Likelihood
|  | 1 | 2 | 3 | 4 | 5
Consequence | 5 | 5 High* | 10 High | 15 High | 20 Critical | 25 Critical
| 4 | 4 Low | 8 Medium | 12 High | 16 High | 20 Critical
| 3 | 3 Low | 6 Medium | 9 Medium | 12 High | 15 High
| 2 | 2 Low | 4 Low | 6 Medium | 8 Medium | 10 High
| 1 | 1 Low | 2 Low | 3 Low | 4 Low | 5 Medium
Severity rule: a consequence of 5 is never below High, however unlikely it is. Without this rule, an event that could drop the whole site scores the same as a near-certain nuisance. That is the best-known weakness of risk matrices. (* marks the cell this rule raises.)
Level |  | Score | What happens next |  | Who accepts
Low |  | 1–4 | Go ahead with normal controls. |  | The Shift lead can accept.
Medium |  | 5–9 | Go ahead with the listed controls and a named owner for each. |  | The Facility manager accepts.
High |  | 10–16, or any consequence 5 | Only with controls in place, hold points and stop conditions. |  | The risk owner, often the Site manager or above, accepts in writing before the work starts.
Critical |  | 17–25 | Don't start. Change the plan until the risk is lower. |  | If it can't be lowered, the decision goes to the highest management level.
Note: Who may accept each level is set by the site's own governance. The roles above are an example.